mmmmmmmnn

* exhaust gas quantity may be reduced if maximum heat recovery is requested. ** on gas turbines with output higher than 2 MW, twin exhaust gas boilers can be applied. *** R -system in case of multiple units **** ECO-sections : see dimensions in the technical documentation. 18

High exhaust gas temperatures occur when an exhaust gas boiler is applied on furnaces and industrial processes where the gasses going into the boiler are above 450°C. Generally, the concept of standard coil sections can be applied for exhaust gas temperatures up till 450°C. With use of special material for the shells of the boiler, higher gas inlet temperatures can be handled with the concept of standard sections but limited to approx. 550°C. For higher temperatures, Clayton Industries uses the concept of the heating coil as used in the fired steam generator product line. The advantage of this construction is that the shell of the boiler is cooled by a "waterwall" coil. This heating coil type boiler can handle a maximum of approx. 15000 Kg/hr of exhaust gas up to 1200°C, depending on the allowable flow resistance on the gas side.

Depending on the amount of flue gasses, the gas temperature and the maximum allowable gas side pressure drop, a certain model of boiler will be chosen. The free space between the tubes depends on the model of boiler. The gas side pressure drop is also determined by the number tube layers and thus by the heating surface. Required heating surface is determined by the required heat output of the boiler. Clayton Industries uses computer programs in order to optimise the sizing of the boilers within the operating parameters as given by the customer. Following data are requested for proper selection of boiler and auxiliary equipment : make :………………………………………...type . ………………………………….. fuel type : o diesel oil : o heavy oil : o gas type : viscosity : ………………… o spark ignition composition : …………….. o dual fuel quantity in kg/hr. :…………………………….or normal m3/hr. :……………………………… ………………………………………………………………… mmWC:……………………………….or Pa (1 Pa = 0.mmWC) :……………………………………. required output of boiler (kW) :…………………..or required steam output (kg/hr.) :……………………………… starting from a feedwater temperature (OC) (90 °C if not known) ……………………………………………. steam pressure in: bar gauge :…………….. or bar absolute : ………………… required output of boiler (kW) : ………………….. water inlet temperature (OC) : ………………… water outlet temperature (OC): ………………… ………………………………………………………………………………………………………………………………………… When above data are available, a budget proposition for the basic heat recovery equipment can be prepared. Please send back this informations to Mr. Peter Vidos, gen. man. of BLOCK Bt .- (H)-9200 Mosonmagyarovar, Ady E. – út 1/a Mandated agent for IRAN E-mail : claykonz@t-online.hu or vidospeter@t-online.hu - mobil : 00 36 20 9578931 - Skype : vidospeter